## Tenderer's Information
Annexure G:Tenderer's Information
Provide bidder's details
No | Description | Details
1 | Company Name
2 | Physical Address
3 | Contact Name
4 | Contact Phone Number
5 | Contact Email Address
6 | Number of Years of Relevant Experience
7 | Company Registration Number
8 | Tax registration Number
9 | Names of Company Directors
10 | Names of Shareholders of the Company

## Qualification & Experience
Annexure H: Qualifications and Experience of Proposed Key Personnel
Provide proposed key personnel academic qualifications and relevant experience. Submit abridged CV,Copies Of Academic Qualifications and Valid ERB Certificates or equivalent
No | Resource Name | Role | Academic Qualification | Years of relevant Experience | Number of years with the Company
1
2
3
4
5
6
7
8
9
10

## Customer Reference.
Annexure I: Customer References
Provide information about customers where similar services have been rendered . Also provide reference letters from at least three(3) customers
NO | Description | Customer A | Customer B | Customer C | Customer D | Customer E
1 | Company Name
2 | Physical Address
3 | Contact Name
4 | Contact Phone Number
5 | Contact Email Address
6 | Description of Services rendered
7 | Duration of Maintenance support Services

## Sub Contractor's Information
Annexure J: Sub Contractor Information
Provide Sub Contractor's details if any:
No. | Name of Sub Contractor | Number of Years working with the subcontractor | Scope of Work to be Subcontracted | Physical Address,Contact name,telephone,email) | Years of Experience of Sub contractor | Qualifications & Experience of Proposed Personnel | Name of Customer where you have delivered projects with the subcontactor
1
2
3
4
5
6
7
8
9
10

## BOQ
Annexure K: Bill Of Quantities
Provide price for each work breakdown structure. Submit a Quotation in your Company letter head .
No. | Area | Task | Frequency | Unit Price (BWP) | Annual Price(BWP) | 36 Months Price(BWP)
1 | Substations and Switchgear Assemblies: RMUs (3) and Main LV Room (1) | Ventilation: Visual inspection | Quarterly Maintenance
|  | Enclosures (Indoor): | Biannual Maintenance
a) Security/operational check
b) Visual inspection
|  | a) Switchgear: Infrared scanning | Annual Maintenance
b) Insulation: Visual inspection/clean
c) Insulation: Electrical tests
2 | Battery Tripping Units (3) | a) Lead-acid cell-specific gravity measurements | Quarterly Maintenance
b) Sample connection resistances
c) Torque intercell connectors
|  | a) Capacity test | Annual Maintenance
b) Infrared scanning
3 | Transformers - 11kV/400V Dry-Type (4), Oil type(1) | Cleaning, inspection and insulation testing | 2-Yearly Maintenance
|  | Turns-ratio test | 3-Yearly Maintenance
4 | Motor Control Centres (3) and Motor Control Panels | a) Infrared scanning | Annual Maintenance
b) Enclosures: visual Inspection/clean
c) Bus bar, wiring, and terminal connections:
i. Visual inspection of insulators
ii. Visual inspection of wiring
d) Disconnects:
i. Visual inspection/clean
ii. Operation check
e) Contactors: visual inspection/clean
f) Electrical interlocks: inspection
g) Mechanical interlocks: inspection
|  | a) Bus bar, wiring, and terminal connections: | 2-Yearly Maintenance
i. Check connections for tightness
ii. Electrical tests
b) Motor overload relays, nonthermal type: check connections for tightness
Molded-Case Circuit Breakers (MCCB): Mechanical test
|  | a) Motor overload relays, nonthermal type: | 3-Yearly Maintenance
i. Cleaning
ii. Calibration
iii. Function tests
b) Molded-Case Circuit Breakers (MCCB):
i. Visual inspection/clean;
ii. Electrical test
5 | Main Distribution Boards | a) Switchgear: Infrared scanning | Annual Maintenance
b) Insulation: Visual inspection/clean
|  | Insulation: Electrical tests | 2-Yearly Maintenance
6 | Standby Generators (4) and Changeover Switchgear (4) | Electrical Service: | Annual Maintenance
a) Contact/Pole Resistance or Millivolt Drop Tests:
b) Timers and Relays:
i. Normal source voltage-sensing relay
ii. Engine start sequence
iii. Time delay upon transfer
iv. Alternate source voltage-sensing relay
v. Interlocks and limit switch functions
vi. Time delay and retransfer upon normal power restoration
vii. Engine cool down and shutdown feature
Mechanical Service:
Standby Generator Service
7 | Uninterruptible Power Supply (UPS) System | Visual inspection | Quarterly Maintenance
|  | a) Clean/vacuum cabinets | Biannual Maintenance
b) Check tightness of all electrical connections
c) Check system alarms and indicating lights
Inspect HVAC and check humidity
|  | Infrared Scanning | Annual Maintenance
|  | System tests | 2-Yearly Maintenance
8 | Motors | Vibration analysis | Biannual Maintenance
|  | a) Stator and rotor windings | Annual Maintenance
i. Visual and mechanical inspection/cleaning
ii. Electrical tests
· Windings tests
· Insulation resistance tests
b) Brushes, collector rings and commutators
Visual and mechanical inspection
9 | Grounding Systems and Lightning Protection | a) Visual and physical inspection of grounding and bonding conductors, and associated connections. | Annual Maintenance
b) Check integrity of grounding electrode system.
c) Ground loop impedance test on the equipment-grounding path
Testing of Ground-Fault Protection Devices
10 |  | Electrical Studies | Once in 3 Years
11 | HV switching | On site HV switching | As and when required
12 | Training | Conduct Referesher Trainings and practical on HV switching for DTCB elctricians/Technicians | Annually
Sub Total
Vat (@14%)
Total Price